## BOQ
PROVIDING EXTERNAL ELECTRIFICATION WORKS FOR MMLP PARK, JOGIGHOPA, ASSAM - PHASE-1
BILL OF QUANTITY - 33/11kV INDOOR SUB-STATION-1 Nos FOR PHASE-1
S. No. | Description of Item | Unit | Qty | RATE (RS.) | TOTAL AMOUNT (RS)
1 | 2 | 3 | 4 | 5 | 6
A | Design, Engineering, manufacture, shop testing, supply including packing and forwarding, transportation, delivery at site storage charges 33/11 Kv Sub-Station
1 | POWER TRANSFORMER
i) | Design ,Supply ,Erection Testing & Commissioning 5 MVA, three Phase Power Transformer 33 /11KV ONAN cooled, oil immersed with on load tap changer, outdoor type power transformer with all accessories and fittings complete in all respect as specified in technical specification, Oil for first filling plus 10% extra in non-returnable containers as specified in Technical specification including Lifting Jacks for transformers (Including Type test charges) Etc. Complete in all respect to sucussfully commissioning of Sub-Station. | Nos. | 2 |  | 0
2 | 33 KV VCB INDOOR PANEL
i) | 33kV Indoor switchboard comprising of 3 Nos. Incomer rating of 630 A,36 kV class VCB, 25kA,3 Sec., and 2nos. 630 A,36 kV,VCB Outgoing feeders, 25kA,1 Sec, rating including CT’s, CBT’s,Busbar wiring etc. complete in all respect for the system, including Indoor draw out type PT Panel with Fuse protection of Line PT l.(Incomer - 3Nos.& Outgoing - 2Nos ). Switchboard shall be complete with protection class CT’s, Metering CT’s, Line PT’s, Numerical Protective relays, ammeters, voltmeters, Trivectormeter, Indicating lamps, annunciation etc. alongwith accessories complete in all respect as follows: a)Incoming feeder - 3Nos. b) Outgoing feeder - 2Nos. c) Bus coupler - 1 No. | Set | 1 |  | 0
3 | 11kV VCB INDOOR PANEL
(i) | 11 kV Indoor switchboard comprising of 2 Nos. Incomer rating of 630A,12 kV class VCB,25KA, 3 Sec., 1 No. Bus Coupler rating of 630A, 12 kV class VCB, 25KA, 1 Sec and 8nos. 630 A,12 kV,VCB Outgoing feeders, 25 KA,1 Sec, rating including CT’s,CBT’s,Busbar wiring etc. complete in all respect for the system, including Indoor draw out type PT Panel with Fuse protection of Line PT. Switchboard shall be complete with protection class CT’s, Metering CT’s, Line PT , Numerical type relays, ammeters, voltmeters, Trivector meter, Indicating lamps , annunciation etc. as required as per technical specification. a)Incomer - 2Nos. of rating 630Amp., 25kA b) Outgoing - 8Nos. of rating 630Amp., 25kA c) Bus coupler - 1 No. of rating 630Amp., 25kA | Sets | 1 |  | 0
4 | AFPC Panel : Automatic Power Factor Controller Panel with Capacitor Banks [Indoor Type]
| Supply ,Erection ,Testing and Commissioning of 11 kV APFC Panel with communication provision for Electrical parameters KWH, KVAH,PF,HZ and ON, OFF, TRIP, FAULT, Suitable Ventilation and Temperature Indications and Capacitor Bank :3500KVAR, 11KV, 3 phase capacitor banks with isolators on one bus section of 11KV switch board in star configuration along with cast resin/resin impregnated air cooled series reactors, cast resin neutral CT in a closed container detaied as per technical specification. | Sets | 1 |  | 0
5 | BATTERY BANK
| 110V DC Battery bank (minimum capacity 100AH / 5 hrs).Battery bank shall comprise of standard maintenance free Lead Acid (Plante) cells. Battery Confirms to IS-10918, including all Racks etc.as requires to complete the job. All auxiliaries and accessories complete in all respect as per specification | Sets | 1 |  | 0
6 | BATTERY CHARGER
| Battery charger (Float-cum-Boost charger) suitable for item (5) above with all auxiliaries & accessories complete as per specification | Sets | 1 |  | 0
7 | ACDB
| The ACDB shall cater to all the auxiliary loads requirements of 33 kV switchboard, 11kV Switchboard and LT switchboard, battery charger, ventilation system, exhaust fans, illumination, control supply, Portable sump pump for cable trench and other associated auxiliaries to be provided in the substation. Bidder to note that MCBs used in ACDB shall have short circuit capacity of 50kA for 1 second, comprising of: (i) 415V AC Distribution Board (ACB) comprising of: a) Incomer 2Nos, 200 Amps, 4P, ACB with O/C,E/F protection one for Second Source & One for Station Transformer with 2 Lock Single Key Mechanical interlock– 2 nos. b)MCCB outgoings as per requirement - 15 Nos (63 Amps, 4P – 1 No, 32A 4P- 2No., 16A 4P-5No., 32A, 2P-1no., 20A 2P-3No., 25A 2P-1no., 10A 2P -2No.,) Ratings of ACDB feeders shall be finalized during engineering stage.10% of the total feeders shall be provided as spare feeders for Purchaser’s future use. | Sets | 1 |  | 0
8 | DCDB
| The DCDB shall cater to all the auxiliary loads requirements of 33 kV switchboard control supply, 11 kV Switchboards control supply ,Emergency Lighting for Switchgear Room and Outdoor Switchyard in the substation. Bidder to note that MCBs used in DCDB shall have short circuit capacity of 6KA/3KA for 1 second.(As per IS standards ) i) Incomer 63 Amps, 110 V, DC distribution Board with DC MCB, bus-bar, internal wiring, accessories, etc. complete in all respects as specified in the technical specification. ii) 6 Nos. Outgoing (32 Amps – 2 Nos ,25 Amps - 2 Nos & 10 Amps – 2 Nos.) | Sets | 1 |  | 0
9 | CONTROL CABLES
1100V, PVC insulated, PVC sheathed, FRLS, galvanized steel wire/ strip armoured and Aluminium wire/strip armoured (for CT’s & PT’s) multistranded copper conductor control cable complete as per specification.(Control LT power Cables for tapping power supply for LT auxiliary loads and illumination as described under Battery limit.)
| i) 2 Core, 2.5 sq. mm | RM | 60 |  | 0
| ii) 4 Core, 2.5 sq. mm | RM | 40 |  | 0
| iii) 7 Core, 2.5 sq. mm | RM | 70 |  | 0
| iv) 10 Core, 2.5 sq. mm | RM | 30 |  | 0
| v) 14 Core, 2.5 sq. mm | RM | 30 |  | 0
| vi) 24 Core, 2.5 sq. mm | RM | 30 |  | 0
| vii) 2 Core, 4 sq. mm | RM | 50 |  | 0
| viii) 4 Core, 4 sq. mm | RM | 50 |  | 0
10 | GLANDS & LUGS For Control Cables
| Cable Glands & Lugs for all above cables | Lot | 2 |  | 0
11 | TRAYS
Perforated galvanised Cables trays and ladders including bends, tees, cross connections, reducers, etc., fixing arrangements such as coupler, bolts, nuts and washers, etc., of various sizes and types as per design alongwith accessories complete in all respects
i)Cable trays without covers
| a) 600 mm wide | MTR | 300 |  | 0
| b)300 mm wide | MTR | 300 |  | 0
ii)Cable ladders with out covers
| a)600 mm wide | MTR | 200 |  | 0
| b)300 mm wide | MTR | 200 |  | 0
12 | STATION TRANSFORMERS(11/0.433 KV)
| Supply, installation, connecting, testing and commissioning of 100kVA, 11/0.433kV, ONAN step down outdoor type transformeron on two pole structure including topping of oil if required shall be provided , work shall be complite in all respect as per approved specification. | Nos. | 1 |  | 0
13 | Earthing
Earthing comprising of the following and all required materials complete in all respects as per specification
i | Supply, making earth pits and earthing with Copper earth plate 600 mm x 600 mm x 3mm thick including pipe, funnel and other accessories with all earth work and providing masonry enclosure with cover plate having locking arrangement, watering pipe etc. as per IS: 3043 codes complete as per specification including charcoal & salt, complete as required. | Each | 12 |  | 0
ii. | Supply, making earth pits and earthing with G.I earth plate 600 mm x 600 mm x 6mm thick including pipe, funnel and other accessories with all earth work and providing masonry enclosure with cover plate having locking arrangement, watering pipe etc. as per IS: 3043 codes complete as per specification including charcoal & salt complete as required. | Each | 20 |  | 0
iii. | Supply and Erection of 25 mm X 5 mm copper earth strip in surface / recess/ below ground including soldering etc. as required to complete the job as per specification. | RM | 120 |  | 0
iv. | Supply and Erection of 25 mm X 5 mm tinned G.I. strip in surface / recess/ below ground including soldering etc. as required to complete the job as per specification. | RM | 320 |  | 0
v. | Supply and Erection of 50 mm X 5 mm tinned G.I. strip in surface / recess / below ground inlcuding soldering etc as required to complete the job as per specification. | RM | 360 |  | 0
14 | FIRE FIGHTING AND SAFETY ITEM
| i.Supply of fire buckets 5 Nos. 15 litre capacity duly filleed with fine sand and fixed on an angle iron frame as per requirement of local authorities. The fire buckets shall be painted red from outside and white from inside, including lettered as FIRE with white colour with extra handle at bottom. | Set | 12 |  | 0
| ii.Supply of Rubber hand gloves 11kV grade, as per IS 4770-1968. | Pair | 10 |  | 0
| iii.Supply of Rubber hand glove 33kV grade, as per IS 4770-1968. | Pair | 4 |  | 0
| iv.Supply of standard first aid box as approved by Indian Red Cross Society/ St. John Ambulance Brigade and conforming to IS 2217-1963. | Set | 4 |  | 0
| v.Supply and fixing in position the approved " shock treatment charts" framed in teak wood frame and covered with galss in front as required in two languages (Hindi & English) | Nos | 4 |  | 0
| vi.Supply and fixing Carbon dioxide fire extinguishers of 4.5 kg each as per IS : 2878-1976 and mounting the same on wall by means of suitable hooks. | Nos. | 4 |  | 0
15 | UPS SYSTEM
| 2x10 KVA 3phase input- 1phase output High Performance IGBT/PWM based True-On-Line Double Conversion Microprocessor Controlled Parallel Redundant UPS system – with 60 min backup on each UPS with all related accessories.Batteries 02 bank of sealed maintenance Free (SMF) Exide make of batteries with 65 AH x 20 batteries, Complete, inter-connecting links, DC cable for 5 mtrs distance. Inclusive of freight, Loading & Unloading, Installation & Commissioning | Set | 2 |  | 0
16 | Air Coditioner for Scada Room 3.0 Tonne Capacity (Split Type) inculding voltage Stbiliser ,time delay relays etc. | No | 2 |  | 0
17 | POWER CABLES & TERMINATIONS
Supply ,Erection testing & Commissioning power and control cables. A large Portion shall be laid along tunnel. The tunnel shall be provided with channels. The Cable shall be clamped on these channels. Some Cables shall be laid through cable trenches and certain portion may also be supported with GI Angle
i) | 33kV, 3CX300 Sq mm for Transformer Incomer | Mt | 300 |  | 0
ii) | Termination of 300 sq mm Cable (indoor) | Nos | 8 |  | 0
iii) | Termination of 300 sq mm Cable (outdoor) | Nos | 8 |  | 0
iv) | 11kV, 1CX630 Sq mm for Transformer to 11 KV Panel | Mt | 300 |  | 0
v) | Termination of 1CX630 sq mm Cable (indoor) | Nos | 8 |  | 0
vi) | Termination of 1CX630 sq mm Cable (outdoor) | Nos | 8 |  | 0
vii) | 11kV, 3X95 Sq mm 11 KV XLPE Cable to feed Station Transformer and Capacitor Bank | Mt | 300 |  | 0
viii) | Termination of 3X95 Sq mm 11 KV XLPE Cable (indoor) | Nos | 8 |  | 0
ix) | Termination of 3X95 Sq mm 11 KV XLPE Cable (outdoor) | Nos | 8 |  | 0
B | COMMON MISCELLENOUS WORKS AT JABANG 33/1kV PRIMARY SUBSTATION
1 | Compound walling of identified land by way of Mass Concrete in Foundations and Concrete block Wall of 2 M height | RM | 240 |  | 0
2 | Land development of area (Cutting , filling and leveling etc as per site requirement) | Item | 2 |  | 0
3 | 33/11 kV Power Transformer Foundation | Each | 2 |  | 0
4 | RCC plinth foundation for Station Transformer | Each | 2 |  | 0
5 | Civil Work :Construction of Control Room Building 20 meterX10 meter
| Construction of control Room with required drainage arrangement with inside cable trench excavation RCC column, Foundations, RCC works in super structure in M20/M25 including MS reinforcement Door Windows, Kota stones flooring etc.Fully glazed steel windows, Ventilator, Door of Single shutter 35 mm teak veneer facing flush door etc, including necessary excavation foundations, with bed concrete and painting of outside by cement paint and inside oil bond distemper.(Stone pitching shall be provided for protection of filled earth.) | Sq.mtr. | 400 |  | 0
6 | Construction RCC trenches for Power/Control cables including all accessories to complete the item | Meter | 100 |  | 0
7 | Internal Electrification of Control Room building including all fixtures, DB, Wiring, Air conditioner etc. complete as per specification | Item | 2 |  | 0
8 | Yard Lighting | Item | 2 |  | 0
9 | Sanitary and water supply | Item | 2 |  | 0
10 | Sump Well for water storage 15000 ltr. Capacity | Item | 2 |  | 0
11 | Construction Of Roads | Item | 2 |  | 0
12 | Provision of Main Gate 4meterX2 meter made MS Angle and sheet. | Item | 2 |  | 0
TOTAL = |  |  |  |  | 0

## COST ESTIMATE
INFRASTRUCTURE DEVELOPMENT WORK OF MMLP JOGIBHOPA, ASSAM
COST ESTIMATE - 33/11kV INDOOR SUB-STATION-2 Nos
S. No. | Description of Item | Unit | Qty | RATE (RS.) | TOTAL AMOUNT (RS)
1 | 2 | 3 | 4 | 5 | 6
A. | Design, Engineering, manufacture, shop testing, supply including packing and forwarding, transportation, delivery at site storage charges 33/11 Kv Sub-Station
1 | POWER TRANSFORMER
i) | Design ,Supply ,Erection Testing & Commissioning 5 MVA, three Phase Power Transformer 33 /11KV ONAN cooled, oil immersed with on load tap changer, outdoor type power transformer with all accessories and fittings complete in all respect as specified in technical specification, Oil for first filling plus 10% extra in non-returnable containers as specified in Technical specification including Lifting Jacks for transformers (Including Type test charges) Etc. Complete in all respect to sucussfully commissioning of Sub-Station. | Nos. | 2 | 6603763.82 | 13207527.64
2 | 33 KV VCB INDOOR PANEL
i) | 33kV Indoor switchboard comprising of 1 Nos. Incomer rating of 630 A,36 kV class VCB, 25kA,3 Sec., and 2nos. 630 A,36 kV,VCB Outgoing feeders, 25kA,1 Sec, rating including CT’s, CBT’s,Busbar wiring etc. complete in all respect for the system, including Indoor draw out type PT Panel with Fuse protection of Line PT l.(Incomer - 1Nos.& Outgoing - 2Nos ). Switchboard shall be complete with protection class CT’s, Metering CT’s, Line PT’s, Numerical Protective relays, ammeters, voltmeters, Trivectormeter, Indicating lamps, annunciation etc. alongwith accessories complete in all respect as follows: a)Incoming feeder - 1Nos. b) Outgoing feeder - 2Nos. | Set | 1 | 2308000 | 2308000
3 | 11kV VCB INDOOR PANEL
(i) | 11 kV Indoor switchboard comprising of 2 Nos. Incomer rating of 630A,12 kV class VCB,25KA, 3 Sec., 1 No. Bus Coupler rating of 630A, 12 kV class VCB, 25KA, 1 Sec and 8nos. 630 A,12 kV,VCB Outgoing feeders, 25 KA,1 Sec, rating including CT’s,CBT’s,Busbar wiring etc. complete in all respect for the system, including Indoor draw out type PT Panel with Fuse protection of Line PT. Switchboard shall be complete with protection class CT’s, Metering CT’s, Line PT , Numerical type relays, ammeters, voltmeters, Trivector meter, Indicating lamps , annunciation etc. as required as per technical specification. a)Incomer - 2Nos. of rating 630Amp., 25kA b) Outgoing - 8Nos. of rating 630Amp., 25kA c) Bus coupler - 1 No. of rating 630Amp., 25kA | Sets | 1 | 8150125 | 8150125
4 | AFPC Panel : Automatic Power Factor Controller Panel with Capacitor Banks [Indoor Type]
| Supply ,Erection ,Testing and Commissioning of 11 kV APFC Panel with communication provision for Electrical parameters KWH, KVAH,PF,HZ and ON, OFF, TRIP, FAULT, Suitable Ventilation and Temperature Indications and Capacitor Bank :3500KVAR, 11KV, 3 phase capacitor banks with isolators on one bus section of 11KV switch board in star configuration along with cast resin/resin impregnated air cooled series reactors, cast resin neutral CT in a closed container detaied as per technical specification. | Sets | 1 | 5048750 | 5048750
5 | BATTERY BANK
| 110V DC Battery bank (minimum capacity 100AH / 5 hrs).Battery bank shall comprise of standard maintenance free Lead Acid (Plante) cells. Battery Confirms to IS-10918, including all Racks etc.as requires to complete the job. All auxiliaries and accessories complete in all respect as per specification | Sets | 1 | 432750 | 432750
6 | BATTERY CHARGER
| Battery charger (Float-cum-Boost charger) suitable for item (5) above with all auxiliaries & accessories complete as per specification | Sets | 1 | 360625 | 360625
7 | ACDB
| The ACDB shall cater to all the auxiliary loads requirements of 33 kV switchboard, 11kV Switchboard and LT switchboard, battery charger, ventilation system, exhaust fans, illumination, control supply, Portable sump pump for cable trench and other associated auxiliaries to be provided in the substation. Bidder to note that MCBs used in ACDB shall have short circuit capacity of 50kA for 1 second, comprising of: (i) 415V AC Distribution Board (ACB) comprising of: a) Incomer 2Nos, 200 Amps, 4P, ACB with O/C,E/F protection one for Second Source & One for Station Transformer with 2 Lock Single Key Mechanical interlock– 2 nos. b)MCCB outgoings as per requirement - 15 Nos (63 Amps, 4P – 1 No, 32A 4P- 2No., 16A 4P-5No., 32A, 2P-1no., 20A 2P-3No., 25A 2P-1no., 10A 2P -2No.,) Ratings of ACDB feeders shall be finalized during engineering stage.10% of the total feeders shall be provided as spare feeders for Purchaser’s future use. | Sets | 1 | 291385 | 291385
8 | DCDB
| The DCDB shall cater to all the auxiliary loads requirements of 33 kV switchboard control supply, 11 kV Switchboards control supply ,Emergency Lighting for Switchgear Room and Outdoor Switchyard in the substation. Bidder to note that MCBs used in DCDB shall have short circuit capacity of 6KA/3KA for 1 second.(As per IS standards ) i) Incomer 63 Amps, 110 V, DC distribution Board with DC MCB, bus-bar, internal wiring, accessories, etc. complete in all respects as specified in the technical specification. ii) 6 Nos. Outgoing (32 Amps – 2 Nos ,25 Amps - 2 Nos & 10 Amps – 2 Nos.) | Sets | 1 | 30293 | 30293
9 | CONTROL CABLES
1100V, PVC insulated, PVC sheathed, FRLS, galvanized steel wire/ strip armoured and Aluminium wire/strip armoured (for CT’s & PT’s) multistranded copper conductor control cable complete as per specification.(Control LT power Cables for tapping power supply for LT auxiliary loads and illumination as described under Battery limit.)
i) | 2 Core, 2.5 sq. mm | RM | 60 | 102 | 6120
ii) | 4 Core, 2.5 sq. mm | RM | 40 | 161 | 6440
iii) | 7 Core, 2.5 sq. mm | RM | 70 | 252 | 17640
iv) | 10 Core, 2.5 sq. mm | RM | 30 | 331 | 9930
v) | 14 Core, 2.5 sq. mm | RM | 30 | 448 | 13440
vi) | 24 Core, 2.5 sq. mm | RM | 30 | 741 | 22230
vii) | 2 Core, 4 sq. mm | RM | 50 | 133 | 6650
viii) | 4 Core, 4 sq. mm | RM | 50 | 218 | 10900
10 | GLANDS & LUGS For Control Cables
| Cable Glands & Lugs for all above cables | Lot | 2 | 150000 | 300000
11 | TRAYS
Perforated galvanised Cables trays and ladders including bends, tees, cross connections, reducers, etc., fixing arrangements such as coupler, bolts, nuts and washers, etc., of various sizes and types as per design alongwith accessories complete in all respects
i) | Cable trays without covers
a) | 600 mm wide | m | 300 | 1836 | 550800
b) | 300 mm wide | m | 300 | 1027 | 308100
ii) | Cable ladders with out covers
a) | 600 mm wide | m | 200 | 1000 | 200000
b) | 300 mm wide | m | 200 | 800 | 160000
12 | STATION TRANSFORMERS(11/0.433 KV)
| Supply, installation, connecting, testing and commissioning of 100kVA, 11/0.433kV, ONAN step down outdoor type transformeron on two pole structure including topping of oil if required shall be provided , work shall be complite in all respect as per approved specification. | Nos. | 1 | 198669 | 198669
13 | Earthing
Earthing comprising of the following and all required materials complete in all respects as per specification
i | Supply, making earth pits and earthing with Copper earth plate 600 mm x 600 mm x 3mm thick including pipe, funnel and other accessories with all earth work and providing masonry enclosure with cover plate having locking arrangement, watering pipe etc. as per IS: 3043 codes complete as per specification including charcoal & salt, complete as required. | Each | 12 | 12109 | 145308
ii. | Supply, making earth pits and earthing with G.I earth plate 600 mm x 600 mm x 6mm thick including pipe, funnel and other accessories with all earth work and providing masonry enclosure with cover plate having locking arrangement, watering pipe etc. as per IS: 3043 codes complete as per specification including charcoal & salt complete as required. | Each | 20 | 6321 | 126420
iii. | Supply and Erection of 25 mm X 5 mm copper earth strip in surface / recess/ below ground including soldering etc. as required to complete the job as per specification. | RM | 120 | 1020 | 122400
iv. | Supply and Erection of 25 mm X 5 mm tinned G.I. strip in surface / recess/ below ground including soldering etc. as required to complete the job as per specification. | RM | 320 | 188 | 60160
v. | Supply and Erection of 50 mm X 5 mm tinned G.I. strip in surface / recess / below ground inlcuding soldering etc as required to complete the job as per specification. | RM | 360 | 202 | 72720
14 | FIRE FIGHTING AND SAFETY ITEM
i. | Supply of fire buckets 5 Nos. 15 litre capacity duly filleed with fine sand and fixed on an angle iron frame as per requirement of local authorities. The fire buckets shall be painted red from outside and white from inside, including lettered as FIRE with white colour with extra handle at bottom. | Set | 12 | 1176 | 14112
ii. | Supply of Rubber hand gloves 11kV grade, as per IS 4770-1968. | Pair | 10 | 400 | 4000
iii. | Supply of Rubber hand glove 33kV grade, as per IS 4770-1968. | Pair | 4 | 870 | 3480
iv. | Supply of standard first aid box as approved by Indian Red Cross Society/ St. John Ambulance Brigade and conforming to IS 2217-1963. | Set | 4 | 2822 | 11288
v. | Supply and fixing in position the approved " shock treatment charts" framed in teak wood frame and covered with galss in front as required in two languages (Hindi & English) | Nos | 4 | 157 | 628
vi. | Supply and fixing Carbon dioxide fire extinguishers of 4.5 kg each as per IS : 2878-1976 and mounting the same on wall by means of suitable hooks. | Nos. | 4 | 7760 | 31040
15 | UPS SYSTEM
| 2x10 KVA 3phase input- 1phase output High Performance IGBT/PWM based True-On-Line Double Conversion Microprocessor Controlled Parallel Redundant UPS system – with 60 min backup on each UPS with all related accessories.Batteries 02 bank of sealed maintenance Free (SMF) Exide make of batteries with 65 AH x 20 batteries, Complete, inter-connecting links, DC cable for 5 mtrs distance. Inclusive of freight, Loading & Unloading, Installation & Commissioning | Set | 2 | 613063 | 613063
16 | Air Coditioner for Scada Room 3.0 Tonne Capacity (Split Type) inculding voltage Stbiliser ,time delay relays etc. | No | 2 | 94438 | 188876
17 | POWER CABLES & TERMINATIONS
Supply ,Erection testing & Commissioning power and control cables. A large Portion shall be laid along tunnel. The tunnel shall be provided with channels. The Cable shall be clamped on these channels. Some Cables shall be laid through cable trenches and certain portion may also be supported with GI Angle
i) | 33kV, 3CX300 Sq mm for Transformer Incomer | Mt | 300 | 2310 | 693000
ii) | Termination of 300 sq mm Cable (indoor) | Nos | 8 | 25422 | 203376
iii) | Termination of 300 sq mm Cable (outdoor) | Nos | 8 | 40113 | 320904
iv) | 11kV, 1CX630 Sq mm for Transformer to 11 KV Panel | Mt | 300 | 1116 | 334800
v) | Termination of 1CX630 sq mm Cable (indoor) | Nos | 8 | 7925 | 63400
vi) | Termination of 1CX630 sq mm Cable (outdoor) | Nos | 8 | 9410 | 75280
vii) | 11kV, 3X95 Sq mm 11 KV XLPE Cable to feed Station Transformer and Capacitor Bank | Mt | 300 | 747 | 224100
viii) | Termination of 3X95 Sq mm 11 KV XLPE Cable (indoor) | Nos | 8 | 11010 | 88080
ix) | Termination of 3X95 Sq mm 11 KV XLPE Cable (outdoor) | Nos | 8 | 16000 | 128000
B | COMMON MISCELLENOUS WORKS AT JABANG 33/1kV PRIMARY SUBSTATION
1 | Compound walling of identified land by way of Mass Concrete in Foundations and Concrete block Wall of 2 M height | RM | 240 | 6395 | 1534800
2 | Land development of area (Cutting , filling and leveling etc as per site requirement) | Item | 2 | 900000 | 1800000
3 | 33/11 kV Power Transformer Foundation | Each | 2 | 1500000 | 3000000
4 | RCC plinth foundation for Station Transformer | Each | 2 | 20000 | 40000
5 | Civil Work :Construction of Control Room Building 20 meterX10 meter
| Construction of control Room with required drainage arrangement with inside cable trench excavation RCC column, Foundations, RCC works in super structure in M20/M25 including MS reinforcement Door Windows, Kota stones flooring etc.Fully glazed steel windows, Ventilator, Door of Single shutter 35 mm teak veneer facing flush door etc, including necessary excavation foundations, with bed concrete and painting of outside by cement paint and inside oil bond distemper.(Stone pitching shall be provided for protection of filled earth.) | Sq.mtr. | 400 | 45000 | 18000000
6 | Construction RCC trenches for Power/Control cables including all accessories to complete the item | Meter | 100 | 18000 | 1800000
7 | Internal Electrification of Control Room building including all fixtures, DB, Wiring, Air conditioner etc. complete as per specification | Item | 2 | 200000 | 400000
8 | Yard Lighting | Item | 2 | 62690 | 125380
9 | Sanitary and water supply | Item | 2 | 400000 | 800000
10 | Sump Well for water storage 15000 ltr. Capacity | Item | 2 | 150000 | 300000
11 | Construction Of Roads | Item | 2 | 2500000 | 5000000
12 | Provision of Main Gate 4meterX2 meter made MS Angle and sheet. | Item | 2 | 95000 | 190000
TOTAL = |  |  |  |  | 68154989.64

## RA
RATE ANALYSIS FOR NON SCHEDULE ITEMS
1 | Equipment/Item Name |  | POWER TRANSFORMER
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of 5 MVA, 3Ph Power Tranformer |  | 4577999 | 4577999 | As per budg. Price offer by Voltamp Transformer Limited.
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 824039.82 | 824039.82
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 228899.95
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 228899.95
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 22889.995
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 721034.8425 | 1201725
Final Cost |  |  |  |  | 6603763.82
|  |  |  | or say, | 6603763.82
2 | Equipment/Item Name |  | 33 KV VCB INDOOR PANEL
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of 33 KV VCB Indoor Panel |  | 1600000 | 1600000 | As per budg. Price offer by abb
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 288000 | 288000
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 80000
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 80000
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 8000
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 252000 | 420000
Final Cost |  |  |  |  | 2308000
|  |  |  | or say, | 2308000
3 | Equipment/Item Name |  | 11 KV VCB INDOOR PANEL
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of 11 KV VCB Indoor Panel |  | 5650000 | 5650000 | As per budg. Price offer by abb
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 1017000 | 1017000
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 282500
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 282500
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 28250
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 889875 | 1483125
Final Cost |  |  |  |  | 8150125
|  |  |  | or say, | 8150125
4 | Equipment/Item Name |  | AFPC Panel : Automatic Power Factor Controller Panel with Capacitor Banks [Indoor Type]
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of AFPC Panel |  | 3500000 | 3500000 | As per budg. Price offer by abb
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 630000 | 630000
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 175000
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 175000
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 17500
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 551250 | 918750
Final Cost |  |  |  |  | 5048750
|  |  |  | or say, | 5048750
5 | Equipment/Item Name |  | BATTERY BANK
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Battery Bank |  | 300000 | 300000 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 54000 | 54000
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 15000
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 15000
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 1500
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 47250 | 78750
Final Cost |  |  |  |  | 432750
|  |  |  | or say, | 432750
6 | Equipment/Item Name |  | BATTERY CHARGER
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Battery Charger |  | 250000 | 250000 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 45000 | 45000
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 12500
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 12500
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 1250
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 39375 | 65625
Final Cost |  |  |  |  | 360625
|  |  |  | or say, | 360625
7 | Equipment/Item Name |  | ACDB
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of ACDB |  | 202000 | 202000 | Advance Panel & Switchgears(P) Ltd.
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 36360 | 36360
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 10100
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 10100
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 1010
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 31815 | 53025
Final Cost |  |  |  |  | 291385
|  |  |  | or say, | 291385
8 | Equipment/Item Name |  | DCDB
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of DCDB |  | 21000 | 21000 | Advance Panel & Switchgears(P) Ltd.
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 3780 | 3780
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 1050
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 1050
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 105
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 3307.5 | 5513
Final Cost |  |  |  |  | 30293
|  |  |  | or say, | 30293
CONTROL CABLES
9(i) | Equipment/Item Name |  | 2 Core, 2.5 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 102 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 30% |  | 30.6 | 71.4
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 12.852 | 12.852
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 3.57
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 3.57
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 0.357
| 6 | Contractor's Profit @15% on Sl. No.1 | 15% | 10.71 | 18
Final Cost |  |  |  |  | 102.252
|  |  |  | or say, | 102
9(ii) | Equipment/Item Name |  | 4 Core, 2.5 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 160 |  | POLYCAB- OCT 2017-18
|  | Deduct : Discount @ 30% |  | 48 | 112
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 20.16 | 20.16
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 5.6
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 5.6
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 0.56
| 4 | Contractor's Profit @15% on Sl. No.1 | 15% | 16.8 | 29
Final Cost |  |  |  |  | 161.16
|  |  |  | or say, | 161
9(iii) | Equipment/Item Name |  | 7 Core, 2.5 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 251 |  | POLYCAB- OCT 2017-18
|  | Deduct : Discount @ 30% |  | 75.3 | 175.7
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 31.626 | 31.626
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 8.785
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 8.785
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 0.8785
| 4 | Contractor's Profit @15% on Sl. No.1 | 15% | 26.355 | 45
Final Cost |  |  |  |  | 252.326
|  |  |  | or say, | 252
9(iv) | Equipment/Item Name |  | 10 Core, 2.5 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 330 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 30% |  | 99 | 231
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 41.58 | 41.58
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 11.55
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 11.55
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 1.155
| 4 | Contractor's Profit @15% on Sl. No.1 | 15% | 34.65 | 59
Final Cost |  |  |  |  | 331.58
|  |  |  | or say, | 331
9(v) | Equipment/Item Name |  | 14 Core, 2.5 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 446 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 30% |  | 133.8 | 312.2
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 56.196 | 56.196
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 15.61
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 15.61
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 1.561
| 4 | Contractor's Profit @15% on Sl. No.1 | 15% | 46.83 | 80
Final Cost |  |  |  |  | 448.396
|  |  |  | or say, | 448
9(vi) | Equipment/Item Name |  | 24 Core, 2.5 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 738 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 30% |  | 221.4 | 516.6
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 92.988 | 92.988
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 25.83
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 25.83
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 2.583
| 6 | Contractor's Profit @15% on Sl. No.1 | 15% | 77.49 | 132
Final Cost |  |  |  |  | 741.588
|  |  |  | or say, | 741
9(vii) | Equipment/Item Name |  | 2 Core, 4 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 132 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 30% |  | 39.6 | 92.4
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 16.632 | 16.632
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 4.62
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 4.62
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 0.462
| 6 | Contractor's Profit @15% on Sl. No.1 | 15% | 13.86 | 24
Final Cost |  |  |  |  | 133.032
|  |  |  | or say, | 133
9(viii) | Equipment/Item Name |  | 4 Core, 4 sq. mm Control Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 217 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 30% |  | 65.1 | 151.9
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 27.342 | 27.342
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 7.595
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 7.595
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 0.7595
| 6 | Contractor's Profit @15% on Sl. No.1 | 15% | 22.785 | 39
Final Cost |  |  |  |  | 218.242
|  |  |  | or say, | 218
CABLE TRAY
11 i(a) | Equipment/Item Name |  | 600 mm wide Cable trays without covers
S.N. | [5 empty] | Final Amount
DSR-4.6 |  | Rs./Nos |  |  | 1257
[5 empty] | 1836.2256 | Considering Cost Index
|  | SAY |  |  | 1836
11 i(b) | Equipment/Item Name |  | 300 mm wide Cable trays without covers
S.N. | [5 empty] | Final Amount
DSR-4.6 |  | Rs./Nos |  |  | 703
[5 empty] | 1026.9424 | Considering Cost Index
|  | SAY |  |  | 1027
11 ii(a) | Equipment/Item Name |  | 600 mm wide Cable ladders with out covers
S.N. | [5 empty] | Final Amount
DSR-4.6 |  | Rs./Nos |  |  | 1257
[5 empty] | 1836.2256 | Considering Cost Index
|  | SAY |  |  | 1836.2256
11 ii(b) | Equipment/Item Name |  | 300 mm wide Cable ladders with out covers
S.N. | [5 empty] | Final Amount
DSR-4.6 |  | Rs./Nos |  |  | 703
[5 empty] | 1026.9424 | Considering Cost Index
|  | SAY |  |  | 1026.9424
12 | Equipment/Item Name |  | 100 KVA STATION TRANSFORMERS(11/0.433 KV)
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of 100kVA, 11/0.433kV, ONAN step down outdoor type transformer |  | 141251 | 141251 | KSEB
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 25425.18 | 25425.18
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 7062.55
| 4 | Labor charges @ 2% on Sl.No.1 | 2% | 2825.02
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 494.3785
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 21611.403 | 31993
Final Cost |  |  |  |  | 198669.18
|  |  |  | or say, | 198669
EARTHING
13(i) | Earthing |  | 600 mm x 600 mm x 3mm Earth Pit
S.N. | [5 empty] | Final Amount
DSR-5.6 |  | Rs./Nos |  |  | 8289
[5 empty] | 12108.5712 | Considering Cost Index
|  | SAY |  |  | 12109
13 (ii) | Earthing |  | 600 mm x 600 mm x 6mm Earth Pit
Final Amount
DSR-5.4 |  | Rs./Nos |  |  | 4327
[5 empty] | 6320.8816 | Considering Cost Index
|  | SAY |  |  | 6321
13 (iii) | Earth Strip |  | 25 mm X 5 mm copper earth strip
Final Amount
DSR-5.14 |  | Rs./Nos |  |  | 698
[5 empty] | 1019.6384 | Considering Cost Index
|  | SAY |  |  | 1020
13 (iv) | GI Strip |  | 25 mm X 5 mm tinned G.I. strip
Final Amount
DSR-5.15 |  | Rs./Nos |  |  | 129
[5 empty] | 188.4432 | Considering Cost Index
|  | SAY |  |  | 188
13(v) | GI Strip |  | 50 mm X 5 mm tinned G.I. strip
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of GI Strip / kg |  | 64.2752 |  | DSR-E&M-2912
| 2 | 50x5mm GI Strip @ 2.5kg/Mtr |  | 160.688 | 160.688 |  | 160.688
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 8.0344
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 8.0344
| 5 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 25.3084 | 41
Final Cost |  |  |  |  | 201.688
|  |  |  | or say, | 202
FIRE FIGHTING AND SAFETY ITEM
14(i) | Equipment/Item Name |  | Fire Buckets ,15 litre capacity
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of fire buckets 15 litre capacity |  | 750 | 750 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 135 | 135
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 37.5
| 4 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 118.125 | 291
Final Cost |  |  |  |  | 1176
|  |  |  | or say, | 1176
14(ii) | Equipment/Item Name |  | Rubber hand gloves 11kV grade
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Rubber hand gloves 11kV grade |  | 255 | 255 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 45.9 | 45.9
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 12.75
| 4 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 40.1625 | 99
Final Cost |  |  |  |  | 399.9
|  |  |  | or say, | 400
14(iii) | Equipment/Item Name |  | Rubber hand gloves 33kV grade
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Rubber hand gloves 33kV grade |  | 555 | 555 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 99.9 | 99.9
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 27.75
| 4 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 87.4125 | 215
Final Cost |  |  |  |  | 869.9
|  |  |  | or say, | 870
14(iv) | Equipment/Item Name |  | standard first aid box
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of standard first aid box |  | 1800 | 1800 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 324 | 324
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 90
| 4 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 283.5 | 698
Final Cost |  |  |  |  | 2822
|  |  |  | or say, | 2822
14(v) | Equipment/Item Name |  | shock treatment charts
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of standard first aid box |  | 100 | 100 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 18 | 18
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 5
| 4 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 15.75 | 39
Final Cost |  |  |  |  | 157
|  |  |  | or say, | 157
14(vi) | Equipment/Item Name |  | Carbon dioxide fire extinguishers of 4.5 kg
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Carbon dioxide fire extinguishers of 4.5 kg |  | 4950 | 4950 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 891 | 891
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 247.5
| 4 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 779.625 | 1918
Final Cost |  |  |  |  | 7759
|  |  |  | or say, | 7760
15 | Equipment/Item Name |  | Three Phase UPS system
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of UPS System with Batteries |  | 425000 | 425000 | Riello Power India Pvt. Ltd.
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 76500 | 76500
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 21250
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 21250
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 2125
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 66937.5 | 111563
Final Cost |  |  |  |  | 613063
|  |  |  | or say, | 613063
16 | Equipment/Item Name |  | Air Coditioner for Scada Room 3.0 Tonne Capacity
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Air Coditioner for Scada Room 3.0 Tonne Capacity |  | 63488 | 63488 | Market Rate
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 11427.84 | 11427.84
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 3174.4
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 3174.4 | 3174.4
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 9999.36 | 16348
Final Cost |  |  |  |  | 94438.24
|  |  |  | or say, | 94438
POWER CABLES & TERMINATIONS
17(i) | Equipment/Item Name |  | 33kV, 3CX300 Sqmm POWER CABLE
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 2580 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 35% |  | 980.4 | 1599.6
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 287.928 | 287.928
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 79.98
| 4 | Labor charges @ 2% on Sl.No.1 | 5% | 79.98
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 7.998
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 251.937 | 420
Final Cost |  |  |  |  | 2307.528
|  |  |  | or say, | 2310
17(ii) | Equipment/Item Name |  | Indoor type Cable Termination for 33kV,3CX300 Sqmm Power Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable Termination |  | 34173 |  | Raychem
|  | Deduct : Discount @ 50% |  | 17086.5 | 17086.5
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 3075.57 | 3075.57
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 854.325
| 4 | Labor charges @ as per actual |  | 1500 |  | LS
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 117.7163
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 2787.975 | 5260
Final Cost |  |  |  |  | 25422.07
|  |  |  | or say, | 25422
17(iii) | Equipment/Item Name |  | Outdoor type Cable Termination for 33kV,3CX300 Sqmm Power Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable Termination |  | 55425 |  | Raychem
|  | Deduct : Discount @ 50% |  | 27712.5 | 27712.5
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 4988.25 | 4988.25
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 1385.625
| 4 | Labor charges @ as per actual |  | 1500 |  | LS
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 144.2812
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 4381.875 | 7412
Final Cost |  |  |  |  | 40112.75
|  |  |  | or say, | 40113
17(iv) | Equipment/Item Name |  | 11kV, 1CX630 Sqmm POWER CABLE
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 1248 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 35% |  | 474.24 | 773.76
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 139.2768 | 139.2768
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 38.688
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 38.688
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 3.8688
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 121.8672 | 203
Final Cost |  |  |  |  | 1116.0368
|  |  |  | or say, | 1116
17(v) | Equipment/Item Name |  | Indoor type Cable Termination for 11kV,1CX630 Sqmm Power Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable Termination |  | 8862 |  | Raychem
|  | Deduct : Discount @ 50% |  | 4431 | 4431
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 797.58 | 797.58
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 221.55
| 4 | Labor charges @ as per actual |  | 1500 |  | LS
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 86.0775
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 889.65 | 2697
Final Cost |  |  |  |  | 7925.58
|  |  |  | or say, | 7925
17(vi) | Equipment/Item Name |  | Outdoor type Cable Termination for 11kV,1CX630 Sqmm Power Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable Termination |  | 11008 |  | Raychem
|  | Deduct : Discount @ 50% |  | 5504 | 5504
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 990.72 | 990.72
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 275.2
| 4 | Labor charges @ as per actual |  | 1500 |  | LS
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 88.76
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 1050.6 | 2915
Final Cost |  |  |  |  | 9409.72
|  |  |  | or say, | 9410
17(Vii) | Equipment/Item Name |  | 11kV, 3CX95 Sqmm POWER CABLE
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable/Mtr. |  | 835 |  | POLYCAB- OCT 2017
|  | Deduct : Discount @ 35% |  | 317.3 | 517.7
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 93.186 | 93.186
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 25.885
| 4 | Labor charges @ 5% on Sl.No.1 | 5% | 25.885
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 2.5885
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 81.5378 | 136
Final Cost |  |  |  |  | 746.886
|  |  |  | or say, | 747
17(viii) | Equipment/Item Name |  | Indoor type Cable Termination for 11kV,3CX95 Sqmm Power Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable Termination |  | 13321 |  | Raychem
|  | Deduct : Discount @ 50% |  | 6660.5 | 6660.5
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 1198.89 | 1198.89
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 333.025
| 4 | Labor charges @ as per actual |  | 1500 |  | LS
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 91.6513
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 1224.075 | 3149
Final Cost |  |  |  |  | 11008.39
|  |  |  | or say, | 11010
17(ix) | Equipment/Item Name |  | Outdoor type Cable Termination for 11kV,3CX95 Sqmm Power Cable
S.No. |  | Description | Taxes | Amount(Rs.) | Final Amount(Rs.) | Remarks
SUPPLY PART | Base Price
| 1 | Rate of Cable Termination |  | 20542 |  | Raychem
|  | Deduct : Discount @ 50% |  | 10271 | 10271
Applicable Taxes
| 2 | GST on Sl. No.1 | 18% | 1848.78 | 1848.78
ERECTION PART | Overhead & Erection Charges
| 3 | Overheads @ 5% for (Store, MH, T&P, Contg, Insurance and Transportation) on Sl. No.1 | 5% | 513.55
| 4 | Labor charges @ as per actual |  | 1500 |  | LS
| 5 | GST @ 5% for for Service on Sl. No.3 & 4 | 5% | 100.6775
| 6 | Contractor's Profit @15% on Sl. No.1 & Sl. No. 4 | 15% | 1765.65 | 3880
Final Cost |  |  |  |  | 15999.78
|  |  |  | or say, | 16000
1(i&ii-a&b) | Laying of Cable
FOR 11kV CABLE -120 TO 400Sq.mm
DSR-8.3.2 |  | Rs./Mtr |  |  | 65
[5 empty] | 94.952 | Consider 1.47 esclation for 2 years
or say, |  |  |  |  | 95